{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":32,"n_cols":9,"rows_kept":32,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ARXF-E"]
[]
[]
[]
[]
["","","","","","ARXF20E5V1B","ARXF25E5V1B","ARXF35E5V1B","ARXF42E5V1B"]
["Dimensioni","Unità","","Altezza","mm","556","556","556","556"]
["","","","Larghezza","mm","740","740","740","740"]
["","","","Profondità","mm","343","343","343","343"]
["Peso","Unità","","","kg","24.0","24.0","24.0","28.0"]
["Compressore","Tipo","","","","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing","Compressore ermetico tipo Swing"]
["Campo di funzionamento","Raffrescamento","T. esterna","Min.","°CBS","-10","-10","-10","-10"]
["","","","Max.","°CBS","48","48","48","48"]
["","Riscaldamento","T. esterna","Min.","°CBU","-15","-15","-15","-15"]
["","","","Max.","°CBU","18","18","18","18"]
["Livello pressione sonora","Raffrescamento","","Alta","dBA","46.0","46.0","48.0","48.0"]
["","Riscaldamento","","Alta","dBA","47.0","47.0","48.0","48.0"]
["Refrigerante","Tipo","","","","R-32","R-32","R-32","R-32"]
["","Carica","","","kg","0.420","0.420","0.550","0.750"]
["","Refrigerante-=-Carica-=-TCO2Eq","","","tCO2Eq","0.280","0.280","0.370","0.510"]
["","GWP","","","","675.0","675.0","675.0","675.0"]
["Collegamenti tubazioni","Lunghezza tubazioni","Max.","est. - int.","m","20","20","20","20"]
["","Carica di refrigerante aggiuntivo","","","kg/m","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)","0,02 (per lunghezza delle tubazioni superiore ai 10m)"]
["","Dislivello","int. - est.","Max.","m","12.0","12.0","12.0","12.0"]
["Accessori standard","Installation manual","","","","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1"]
["","Drain plug","","","","1","1","1","1"]
["Alimentazione","Fase","","","","1~","1~","1~","1~"]
["","Frequenza","","","Hz","50","50","50","50"]
["","Tensione","","","V","220-240","220-240","220-240","220-240"]