{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":41,"n_cols":6,"rows_kept":41,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWHT-Q-XSA"]
[]
[]
[]
[]
["","","","","","EWHT100Q-XSA1"]
["Capacità di Raffrescamento","Capacità di Raffrescamento-=-Nom.-=-kW","","","kW","91.68"]
["Controllo capacità","Metodo","","","","Fase"]
["Controllo della capacità","Capacità minima","","","%","50"]
["Potenza assorbita","Raffrescamento","","Nom.","kW","21.22"]
["EER","","","","","4.32"]
["IPLV","","","","","6.66"]
["SEER","","","","","5.98"]
["Dimensioni","Unità","","Profondità","mm","1300"]
["","","","Altezza","mm","1000"]
["","","","Larghezza","mm","1200"]
["Peso","Peso in ordine di marcia","","","kg","451"]
["","Unità","","","kg","431"]
["Rivestimento","Colore","","","","Bianco avorio"]
["","Materiale","","","","Acciaio zincato"]
["Scambiatore calore acqua - evaporatore","Perdita di carico dell’acqua","Raffrescamento","Nom.","kPa","17.7"]
["Compressore","Compressore-=-Quantità","","","","2"]
["","Tipo","","","","Scroll"]
["Campo di funzionamento","Lato acqua","Evaporatore","Min.","°CBS","-15"]
["","","","Max.","°CBS","30"]
["Livello potenza sonora","Raffrescamento","","Nom.","dBA","80.99"]
["Livello pressione sonora","Raffrescamento","","Nom.","dBA","65.4"]
["Refrigerante","Tipo","","","","R-32"]
["","GWP","","","","675"]
["","Carica","","","kg","7"]
["","Circuiti","","Quantità","","1"]
["Attacchi tubazioni","Ingresso/uscita acqua evaporatore (DE)","","","","3\""]
["Alimentazione","Fase","","","","3"]
["","Frequenza","","","Hz","50"]
["","Tensione","","","V","400"]
["","Gamma di tensione","","Min.","%","-10"]
["","","","Max.","%","+10"]
["Unità","Corrente di spunto","","Max.","A","221"]
["","Corrente di funzionamento","Raffresc.","Nom.","A","36.9"]
["","","","Max.","A","62"]
["","Corrente max. unità per dimensionamento cavi","","","A","68"]