{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXT-ATV3C"]
[]
[]
[]
[]
["","","","","","FWXT10ABTV3C","FWXT15ABTV3C","FWXT20ABTV3C","FWXT10AATV3C (Archived)","FWXT15AATV3C (Archived)","FWXT20AATV3C (Archived)"]
["Dimensioni","Unità","","Larghezza","mm","","","","902","1,100","1,300"]
["","","","Profondità","mm","","","","128","128","128"]
["","","","Altezza","mm","","","","335","335","335"]
["Rivestimento","Colore","","","","","","","RAL 9003","RAL 9003","RAL 9003"]
["Peso","Unità","","","kg","","","","14.0","16.0","19.0"]
["Power supply","Fase","","","","","","","1~","1~","1~"]
["","Frequenza","","","Hz","","","","50","50","50"]
["","Tensione","","","V","","","","230","230","230"]
["Capacità di raffrescamento","7/12°C","","Min.","kW","0.49","0.62","0.70"]
["","","","Med.","kW","0.88","1.08","1.21"]
["","","","Capacità di raffrescamento-=-7/12°C-=-Max.-=-kW","kW","1.24","1.61","1.94"]
["Capacità di raffrescamento sensibile","7/12°C","","Min.","kW","0.37","0.52","0.57"]
["","","","Med.","kW","0.70","0.86","1.02"]
["","","","Max.","kW","0.98","1.27","1.52"]
["Capacità di riscaldamento","45/40°C","","Min.","kW","0.55","0.79","0.74"]
["","","","Med.","kW","1.00","1.36","1.55"]
["","","","Max.","kW","1.50","2.01","2.13"]
["Potenza assorbita","Min.","","","kW","0.01","0.01","0.01"]
["","Med.","","","kW","0.01","0.01","0.01"]
["","Max.","","","kW","0.02","0.02","0.03"]
["Velocità del ventilatore","Min.","","","giri/min","680.00","680.00","680.00"]
["","Med.","","","giri/min","1100.00","1100.00","1100.00"]
["","Max.","","","giri/min","1500.00","1500.00","1500.00"]
["Rivestimento","Colore","","","","RAL 9003","RAL 9003","RAL 9003"]
["","Materiale","","","","Lamiera","Lamiera","Lamiera"]
["Dimensioni","Unità","","Altezza","mm","335","335","335"]
["","","","Larghezza","mm","902","1102","1302"]
["","","","Profondità","mm","128","128","128"]
["","Unità imballata","","Altezza","mm","490","490","490"]
["","","","Larghezza","mm","1030","1230","1430"]
["","","","Profondità","mm","210","210","210"]
["Peso","Unità","","","kg","14","16","19"]
["","Unità imballata","","","kg","15","17","20"]
["Imballaggio","Materiale","","","","Cartone","Cartone","Cartone"]
["Guarnizione","Peso","","","kg","1","1","1"]
["Scambiatore di calore","Quantità","","","","1","1","1"]
["","Volume batteria interna","","","l","0.5","0.61","0.77"]
["","Carica","","Pressione d'esercizio","bar","10","10","10"]
["Circuito idraulico","Diametro attacchi delle tubazioni","","","in","3/4","3/4","3/4"]
["","Materiale tubazione","","","","RAME","RAME","RAME"]
["","Pressione","Riscaldamento","Max.","bar","10","10","10"]
["Circuito idraulico - perdita di carico dell’acqua","Riscaldamento","45/40°C","Min.","kPa","5.10","4.81","6.00"]
["","","","Med.","kPa","12.00","6.30","6.40"]
["","","","Max.","kPa","16.30","7.20","8.10"]
["","Raffrescamento","7/12°C","Min.","kPa","4.80","4.70","5.50"]
["","","","Med.","kPa","10.50","5.60","5.40"]
["","","","Max.","kPa","11.70","5.10","5.30"]
["Circuito idraulico - portata d’acqua","Riscaldamento","45/40°C","Min.","kg/h","100.00","140","150.00"]
["","","","Med.","kg/h","170.00","240","300.00"]
["","","","Max.","kg/h","260.00","350","420.00"]
["","Raffrescamento","7/12°C","Min.","kg/h","80.00","110","120.00"]
["","","","Med.","kg/h","150.00","190","210.00"]
["","","","Max.","kg/h","210.00","280","330.00"]
["Potenza sonora","Min.","","","dBA","35","36","37"]
["","Med.","","","dBA","46","47","48"]
["Livello di potenza sonora","Max.","","","dBA","53.0","54.0","55.0"]
["Campo di funzionamento","Riscaldamento","Lato acqua","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Raffrescamento","Lato acqua","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Installazione in spazi interni","T. esterna","Min.","°CBS","0","0","0"]
["","","","Max.","°CBS","45","45","45"]
["Sistemi di controllo","Telecomando infrarossi","","","","Per FWXT-ATV3(C)(CL)","Per FWXT-ATV3(C)(CL)","Per FWXT-ATV3(C)(CL)"]
["","Integrato sull'unità interna","","","","Sì","Sì","Sì"]
["Alimentazione","Fase","","","","1~","1~","1~"]
["","Frequenza","","","Hz","50","50","50"]
["","Tensione","","","V","230","230","230"]
["Potenza assorbita","Max.","","","W","19","20","29"]
["","Stand-by","","","W","3","4","5"]
["Corrente","Max. corrente di funzionamento","","Riscaldamento","A","0.16","0.18","0.24"]
["","","","Raffresc.","A","0.16","0.18","0.24"]