{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":20,"n_cols":8,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","GSIEKA"]
[]
[]
[]
[]
["","","","GSIEKA15018","GSIEKA10009","GSIEKA20024","GSIEKA25030","GSIEKA35530"]
["Corrente erogata (massima)","","","8,2A","4,1A","10,9A","13,6A","13,6A"]
["Unità collegabile","","","VAM250FCVE(9), VAM350FCVE","VAM150FCVE(9)","VAM350-500J7VEB, VAM500-650FCVE","VAM650-800-1000J7VE, VAM1500-2000J7VEB, VAM800-1000FCVE","VAM1500-2000J7VEB, VAM1500-2000FCVE"]
["Indicatori a LED","","","LED 1 flashing every 5 sec - Heater is starting up, LED 1 flashing every sec - Ari flow detected, heating allowed, LED 1 OFF - No power supply or no flow, LED 1 ON - Problem with duct temperature sensor, setpoint potentiometer or PTC airflow sensor, LED 2 OFF - Heater is not operating, LED 2 ON - Heater is operating","LED 1 flashing every 5 sec - Heater is starting up, LED 1 flashing every sec - Ari flow detected, heating allowed, LED 1 OFF - No power supply or no flow, LED 1 ON - Problem with duct temperature sensor, setpoint potentiometer or PTC airflow sensor, LED 2 OFF - Heater is not operating, LED 2 ON - Heater is operating","LED 1 flashing every 5 sec - Heater is starting up, LED 1 flashing every sec - Ari flow detected, heating allowed, LED 1 OFF - No power supply or no flow, LED 1 ON - Problem with duct temperature sensor, setpoint potentiometer or PTC airflow sensor, LED 2 OFF - Heater is not operating, LED 2 ON - Heater is operating","LED 1 flashing every 5 sec - Heater is starting up, LED 1 flashing every sec - Ari flow detected, heating allowed, LED 1 OFF - No power supply or no flow, LED 1 ON - Problem with duct temperature sensor, setpoint potentiometer or PTC airflow sensor, LED 2 OFF - Heater is not operating, LED 2 ON - Heater is operating","LED 1 flashing every 5 sec - Heater is starting up, LED 1 flashing every sec - Ari flow detected, heating allowed, LED 1 OFF - No power supply or no flow, LED 1 ON - Problem with duct temperature sensor, setpoint potentiometer or PTC airflow sensor, LED 2 OFF - Heater is not operating, LED 2 ON - Heater is operating"]
["Funz. relè","","","230VAC/20A","230VAC/20A","230VAC/20A","230VAC/20A","230VAC/20A"]
["Diametro canalizzazione","mm","","150","100","200","255","355"]
["Capacità","kW","","1.8","0.9","2.4","3.0","3.0"]
["Fori di montaggio","","","150mm","100mm","200mm","250mm","355mm"]
["Temp. esterna max. vicino alla morsettiera","","","50°C","50°C","50°C","50°C","50°C"]
["Sensore di temperatura","","","10 kΩ at 25°C","10 kΩ at 25°C","10 kΩ at 25°C","10 kΩ at 25°C","10 kΩ at 25°C"]
["Ingresso setpoint BMS","","","0-10VDC","0-10VDC","0-10VDC","0-10VDC","0-10VDC"]
["Intervallo controllo temperatura","","","-10…50°C","-10…50°C","-10…50°C","-10…50°C","-10…50°C"]
["Fusibile di sicurezza","","","250V/315mA","250V/315mA","250V/315mA","250V/315mA","250V/315mA"]
["Power supply","Frequenza","Hz","50/60","50/60","50/60","50/60","50/60"]
["","Tensione","V","230","230","230","230","230"]